Heat Shield Insulation (Welded) - Design: HS1200FF-W (HS649C-FF-W)

Applications: “WASH-DOWN” / “SANITARY”, Ovens, Kettles, Vessels, Equipment Heads, Pumps, 
Piping, Valves.

Service: Process Markets (Food Processing)

Maximum Service Temperature: This design is to act as a Thermal Barrier with a maximum service temperature of 1200˚F (649˚C).

Purpose: Shannon Thermal Heat Shield Insulation is a “Self-Contained”, CAD designed, CNC produced, high quality engineered insulation system designed to save energy, retain radiant heat, minimize insulation maintenance and improve the surrounding work environment. Shannon Thermal Heat Shield Insulation is “Non-Porous”, weather and chemical resistant. Shannon Heat Shield is flexible, easy to install, remove and reinstall allowing easy service. The key benefit is “Re-Usability”.

Blanket Components: The Outer Jacketing consists of a layer of Stainless Steel Type 304 Sheet Foil .002” (.05mm) thickness. The inner jacket consists of a layer of Stainless Steel Type 304 Sheet Foil .002” (.05mm) thickness. The Insulation Material is an 11 lb/ft3 (176.2 kg/m3) Fiberglass Needled Mat – Type “E” Fiber and or a 7.5 lb/ft3 (120.1 kg/m3) density, Non-Woven Manniglass® fiberglass. The insulation filler is encapsulated by inner and outer stainless steel sheet foil, “spot welded” together, producing a self-contained blanket system. The Shannon Thermal Heat Shield Insulation will include an integral fastener for easy install and removal.

Blanket Construction: Heat Shield construction shall be a “Seam Welded” construction. Stainless Steel Sheet Jacket materials will be drawn out, to match at the outer jacket edge. Jacketing materials will be folded under (Lipped) and “Spot Welded” and or “Hermetic Spot Welded” at the closure seam. Spot welding will be at most 1/8” (3.2mm) spacing between Welds. Cutouts edges, Slits and Complex Edges will require Tack Welds at most 1” (25.4mm) O.C.

No “On-Site Fabrication” to assure high quality.

ID Plate: For easy identification and location, a stainless steel or aluminum name plate tag is riveted to each Heat Shield piece. 1/8” (0.32CM) embossed lettering shows location, description, size, pressure rating and tag number sequence. Each Heat Shield will include an I.D. Plate.

Design Approach: All items insulated will require a site visit prior to bid submittal. Each item must be field measured for “Custom Fitting” to existing field conditions. Each item must be tagged and or marked for installation reference. At the time of installation, Heat Shield must have a corresponding tag on the Heat Shield and must match to an existing tag on the fitting. No standard Heat Shield designs will be accepted. This will assure a “Custom Fit” design for maximum thermal efficiency.

Blanket Weight: Any one piece will not exceed 40lbs (18 KG) in weight.

Blanket Overlap: To minimize heat loss, the Heat Shield will extend beyond mating flanges unto existing insulation for a minimum of 2” (5cm). Where Heat Shield cannot fit over existing oversized insulation, Heat Shield will butt up to existing insulation with a friction fit closing seam. All sections of pipes will be insulated and open gaps are not acceptable. Heat Shield diameters which are 1.5” (2.5cm) or larger than existing insulation must be end capped to eliminate open air void.

Leak Accommodations:  To accommodate a leak and detect its origin, blankets will have a low point stainless steel or brass drain grommet or the design will include a low point blanket seam.

CAD / CNC Requirement: Each Heat Shield insulation project will include an instruction package shipped with the Heat Shield material. This package will include Assembly Drawings identifying piece location, a Material List of all pieces and Instructions for Installation on how Heat Shield will be installed. Accurate CAD files & project records must be kept by the manufacturer. For a minimum of ten years these records will assure accuracy in re-ordering and part replacement. All Heat Shields are to be CAD designed / CNC produced to assure the highest quality and precise fit.

Manufacture Origin:  Blanket & Blanket Components must be made in the U.S.A.

SELECT YOUR: FASTENER

STANDARD FASTENER “WIRETWISTS”: A stainless steel wire (0.50 mm2) 20 Gauge, will be doubled up and twisted in a spiral fashion, with a minimum of 5-7 twists/inch (2-3 twists/cm). Wiretwist length will be 16” (40cm) or longer. The Wiretwist will be secured to the lacing pin at the pin stem. Pin stems will be 2.5 mm2 (14 gauge). Wiretwists will be spaced 6” (15cm) on center along closing seams with matching lacing pins to lace and secure to.

FASTENER OPTIONS:

Metal Spring Tensioner – 5/16” Dia.(7.94mm) - 3.8lb/in (0.07kg/mm) Rating – 2 ½” (6.35cm) Length, combined with 2 each 1 ¼” (3.2cm) Diameter stainless steel split rings, fastened to the Heat Shield edge, 2” (5cm) from the Heat Shield edge. The spring tensioner will be secured to the lacing pin at the spring ring edge. Pin stems will be 14 gauge (2.5 mm2). The Metal Spring Tensioner will be spaced at most 6” (15 cm) on center along closing seams with matching lacing pins for securing. The Metal Spring Tensioner will be positioned between the outer jacketing & outer layer of the insulation.

Blanket Design Warranty:
Thermal Blankets will accommodate vibration probes, gauges, tubing, piping, brackets, etc. and fit correctly for optimum performance as per the design specification provided in the quotation process. In addition, for 18 months thermal blanket manufacturer will cover the cost of replacing the blanket should the failure be due to premature degradation of any component utilized in the blanket construction, as well as any defects due to poor workmanship.

Select: Surface Temperature to Blanket Thickness Reference

Target a Surface Temperature below 145˚F:

| Operating Temperature | Thickness | Surface Temperature | Thickness | Surface Temperature | Thickness | Surface Temperature |
| --- | --- | --- | --- | --- | --- | --- |
| 315.6˚ C (600˚ F) | 25 mm( 1") | 69.2˚ C (156.5˚ F) | 50 mm (2") | 59.8˚ C (139.6˚ F) | 65 mm (2.5") | 53.6˚ C (128.4˚ F) |
| 371˚ C (700˚ F) | 40 mm (1.5") | 72.5˚ C (162.5˚ F) | 40 mm (1.5") | 59.7˚ C (139.5˚ F) | 50 mm (2") | 52.2˚ C (126.0˚ F) |
| 427˚ C (800˚ F) | 40 mm (1.5") | 79.2˚ C (174.6˚ F) | 50 mm (2") | 68.1˚ C (154.5˚ F) | 65 mm (2.5") | 60.7˚ C (141.2˚ F) |
| 482˚ C (900˚ F) | 40 mm (1.5") | 90.3˚ C (194.5˚ F ) | 50 mm (2") | 77.2˚ C (171.0˚ F ) | 65 mm (2.5") | 68.6˚ C (155.4˚ F ) |
| 538˚ C (1000˚ F) | 50 mm (2") | 87.4˚ C (189.4˚ F) | 65 mm (2.5") | 77.3˚ C (171.2˚ F) | 80 mm (3") | 70.1˚ C (158.1˚ F) |
| 593˚ C (1100˚ F) | 50 mm (2") | 98.7˚ C (209.7˚ F) | 65 mm (2.5") | 87.1˚ C (188.8˚ F) | 80 mm (3") | 78.7˚ C (173.7˚ F) |
| 649˚ C (1200˚ F) | 50 mm (2") | 114.4˚ C (237.9˚ F) | 65 mm (2.5") | 103.3˚ C (217.9˚ F) | 80 mm (3") | 92.1˚ C (197.8˚ F) |
| * The above referenced Cold Face Surface Temperatures should be used as guidelines for Blanket/Heat Shield insulation thickness design. |
| * The Cold Face Surface Temperature of the Blanket/Heat Shield should approach surrounding ambient temperature conditions. |
| * The economic thickness of the Blanket/Heat Shield should consider Blanket/Heat Shield cost, thermal performance and Blanket/Heat Shield design constraints. |
| * The above referenced Cold Face Surface Temperatures should be used as guidelines for Blanket/Heat Shield insulation thickness design. |

SELECT YOUR: Testing Requirements

ASTM C 335	Standard Test Method for Steady-State Heat Transfer Properties of Pipe Insulation.

ASTM E 1222 – 90	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation - USA

ISO 15665	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation – Int’l

ASTM C 1045 – 07	Standard Practice for Calculating Thermal Transmission Properties under steady state conditions

UL 1709		Standard Fire Test of Protection Materials for MOV / Structural Steel

ASTM E-84-17	Surface Burning Characteristics of Building Materials (Flame Spread & Smoke)

ASTM E-136	Combustion Characteristics of Building Materials / Fire Test Response

ASTM D3787	Burst Strength Evaluation for ASTM F1138 – Spray Shield Compliance