Thermal Blanket Design: LT300LFP-EF (LT149C-LFP-EF)

Applications: Sanitary – “Non-Fibrous” Requirement
Steam Process Piping, Gate Valves, Condensate Pumps, Pasteurizers, Pressure Reducing Valves, Control Valves, Heat Exchangers and Strainers.

Service: Steam & Hot Water Systems subjected to a sanitary wash down condition: Food Grade 
and Sanitary

Maximum Service Temperature: This design is to act as a Thermal Barrier up to 300˚F (149˚C).

Purpose: Shannon Thermal Blankets are a custom fit high quality engineered insulation system designed to save energy, retain radiant heat, minimize insulation maintenance and improve the surrounding work environment. Shannon-INSULTECH® is designed for use in the Food Processing Industry, where a Non-Porous, Non-Fibrous, vapor barrier blanket system can be chemically sanitized, “Sanitary Wash-Down”. The PTFE Teflon® Film Jacketing Complies with the Regulations of the FDA - Reference 21 CFR 177.1550 Standards for Components of Articles Intended to come in Direct Contact with Food. INSULTECH® is flexible and easy to install, remove and reinstall allowing easy access to surfaces.

Blanket Components: The Outer and Inner Jacketing is a 13.5 oz/yd² (459 g/m²) 100 percent PTFE CrossFilm® Laminate. The Insulation Core consists of Aerocel® EPDM Elastomeric Closed Cell Foam Insulation. Aerocel®, Type 1, EF Insulation will be encapsulated by the inner and outer jacketing, with a double sewn construction, producing a “Self-Contained Blanket Insulation System”. The design includes Integral Fasteners for install & removal.

Blanket Construction: Blanket construction shall be a “Double Sewn” lock stitch with a minimum 4-5 stitches/inch (3 stitches/cm). All raw jacket edges will have a tri-fold PTFE Teflon® Laminate binding. No raw cut jacket edge will be exposed. Stitching will be pure PTFE Teflon® 3-Ply thread. No “On-Site Fabrication” to assure high quality.

ID Plate: For easy identification and location, a stainless steel or aluminum name plate tag is riveted to each blanket piece. 1/8” (0.32CM) embossed lettering shows location, description, size, pressure rating and tag number sequence. Each blanket will include an I.D. Plate.

Design Approach: Thermal Blankets will be custom fit to match each specific component geometry. “Generic Designs” are not acceptable. Thermal Blankets will be a self-contained insulation system with an integral fastener to allow for easy access, removal and re-installation.

Blanket Weight: Any one piece will not exceed 40lbs (18 KG) in weight.

Blanket Overlap: To minimize heat loss, the blanket will extend beyond mating flanges unto existing insulation for a minimum of 2” Inches. Where blanket cannot fit over existing oversized insulation, blanket will butt up to existing insulation with a friction fit closing seam. All sections of pipes will be insulated and open gaps are not acceptable. Blanket diameters which are 2” or larger than existing insulation must be end capped to eliminate open air void.

Leak Accommodations:  To accommodate a leak and detect its origin, blankets will have a low point stainless steel or brass drain grommet or the design will include a low point blanket seam.

CAD / CNC Requirement: Thermal Blanket Insulation will require CAD Drawing Submittals to assure accuracy of design. Upon receipt of project contract, each item must be field measured, tagged and “Custom Fitted” to assure a quality fit and finish. All blankets are to be CAD designed / CNC produced to assure the highest quality, precise fit and electronic CAD filing retrieval for future replacement.

SELECT YOUR: FASTENER

1.) STANDARD “WIRETWIST” FASTENER: A stainless steel wire 0.50 mm² (20 Gauge) will be doubled up and twisted in a spiral fashion, with a minimum of 5-7 twists/inch (3-4 twists/cm). Wiretwist length will be 16” (40cm) or longer. The Wiretwist will be secured to the lacing pin at the pin stem. Pin stems will be 2.5 mm² (14 gauge). Wiretwists will be spaced 6” (15cm) on center along closing seams with matching lacing pins to lace and secure to.

Additional FASTENING OPTIONS

2.) Stainless Steel Double “D” Ring Strap: A 1.5”(3.8cm) wide LFP composite 20 mil thick Strap 4-3/4” (12cm) overall long stationary strap is folded with two 1.5”(3.8cm) in width stainless steel “D” rings “Heat Sealed” to the outer surface of the jacket. This is placed ½” (1cm) from the closing seam edge. The pull down strap, minimally 14” (36cm) long, of the same material is heat sealed to the outer jacket 3” (4.8cm)  in from the closing seam edge. Both matching straps are spaced along the closing seam edge no greater than 8” (20cm) apart. All closing seams have a 1.5”(3.8cm) extended LFP flap, which is placed along the stationary strap side of the closing seam.

3.) Non-Metallic Side Release Buckle and Strap: Blanket fasteners will be 1 1/2” Delrin Side Release Buckles with 1.5”wide LFP composite 20 mil thick Straps. The Buckle strap will be a minimum of 5-1/2” long and will be heat sealed to the outer surface for a minimum of 5” in length. A matching pull strap will also be “Heat Sealed” on the outer jacket surface and will match up to the Buckle Strap. The pull strap will be a minimum of 14”.

| Blanket Thickness Surface Temperature Reference: |
| --- |
| Operating Temperature | Thickness | Surface Temperature | Thickness | Surface Temperature | Thickness | Surface Temperature |
| 121˚ C (250˚ F) | 25 mm( 1") | 37.9˚ C (100.2˚ F) | 40 mm( 1.5") | 33.3˚ C (92.0˚ F) | 50 mm (2") | 30.8˚ C (87.4˚ F) |
| 149˚ C (300˚ F) | 25 mm( 1") | 42.6˚ C (108.6˚ F) | 40 mm (1.5") | 36.8˚ C (98.2˚ F) | 50 mm (2") | 33.5˚ C (92.3˚ F) |
| * The above referenced Cold Face Surface Temperatures should be used as guidelines for blanket insulation thickness design. |
| * The Cold Face Surface Temperature of the blanket should approach surrounding ambient temperature conditions. |
| * The economic thickness of the blanket should consider blanket cost, thermal performance and blanket design constraints. |
| * Heat Loss Calculations are based on a 21.1˚ C (70˚ F) ambient temperature using a flat surface condition. |

Blanket Design Warranty:
Thermal Blankets will accommodate vibration probes, gauges, tubing, piping, brackets, etc. and fit correctly for optimum performance as per the design specification provided in the quotation process. In addition, for 18 months thermal blanket manufacturer will cover the cost of replacing the blanket should the failure be due to premature degradation of any component utilized in the blanket construction, as well as any defects due to poor workmanship.

Manufacture Origin:  Blanket & Blanket Components must be made in the U.S.A.

SELECT YOUR: Testing Requirements

ASTM C 335	Standard Test Method for Steady-State Heat Transfer Properties of Pipe Insulation.

ASTM E 1222 – 90	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation - USA

ISO 15665	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation – Int’l

ASTM C 1045 – 07	Standard Practice for Calculating Thermal Transmission Properties under steady state conditions

UL 1709		Standard Fire Test of Protection Materials for MOV / Structural Steel

ASTM E-84-17	Surface Burning Characteristics of Building Materials (Flame Spread & Smoke)

ASTM E-136	Combustion Characteristics of Building Materials / Fire Test Response

ASTM D3787	Burst Strength Evaluation for ASTM F1138 – Spray Shield Compliance