Heat Shield Specification Design: LT500HS-AG (LT260C-HS-AG)

Applications: Steam Traps, Steam Manifolds, Condensate Manifolds, Boiler Doors.

Service: Heat Shield Insulation for “Steam Traps & Steam Specialties”

Maximum Service Temperature: 500˚F (260˚C)

Purpose: Shannon-INSULTECH® Heat Shield is a cost effect thermal insulation solution, used on equipment, machinery and surfaces not exceeding 500˚F. Thermal “Heat Shield” exposure can be indoors and outdoors. Shannon-INSULTECH® Heat Shield is weather / water resistant, ideal for commercial / industrial settings. Shannon-INSULTECH® Heat Shield is a cost-effective insulation design with many of the features typical of a self-contained INSULTECH® Blanket Insulation design.

Blanket Components: The Outer Jacketing is composed of 9.5oz/yd² (323g/m²) Aluminized Vacuum Metallized Fiberglass Cloth.  The Insulation Material is 1/8”-1/4” Thick (3.18mm-6.36mm) Non-Woven Glass Fiber.

Blanket Construction: Shannon Heat Shield Insulation construction shall be double sewn lock stitch with a minimum 7 stitches/inch (2.8 stitches/CM). All raw jacket edges will have a tri-fold fiberglass cloth binding. No raw cut jacket edge will be exposed. Stitching will be done with 100% PTFE Teflon® thread or PTFE Teflon® fiberglass thread. No “On-Site Fabrication” to assure high quality.

ID Plate: For ease of identification and location, an aluminum or stainless-steel name plate tag will be riveted to each blanket piece. 1/8” (3.2mm) Embossed lettering will include equipment model, description, size, rating and tag number sequence. The tag will appear in a visible location on the exterior surface of the heat shield blanket.

Design Approach: Thermal Blankets will be custom fit to match each specific component geometry. “Generic Designs” are not acceptable. Thermal Blankets will be a self-contained insulation system with an integral fastener to allow for easy access, removal and re-installation.

Blanket Weight: Any one piece will not exceed 40lbs (18 kg) in weight.

Blanket Overlap: Thermal blanket will extend beyond the mating flange onto existing insulation for a minimum of 2” (5 cm). Fitting sizes 6” or more must have a minimum 4” (10 cm) overlap. Open gaps are not acceptable.

Leak Accommodations: To accommodate a leak and detect its origin, blankets will have a low point stainless steel/brass drain grommet or the design will include a low point blanket seam.

CAD / CNC Requirement: Thermal Blanket Insulation will require CAD Drawing Submittals to assure accuracy of design. Upon receipt of project contract, each item must be field measured, tagged and “Custom Fitted” to assure a quality fit and finish. All blankets are to be CAD designed / CNC produced to assure the highest quality, precise fit and electronic CAD filing retrieval for future replacement.

Manufacture Origin:  Blanket & Blanket Components must be made in the U.S.A.

SELECT YOUR: FASTENER

Velcro® Flaps: Jacketing flaps are secured closed by the utilization of Hook/Loop (Velcro®) fasteners. A 2” (5 cm) wide section of the Hook portion of the fastener will be stitched to the outer surface of the blanket. A 2” (5 cm) wide section of the Loop portion will be aligned and stitched on the mating inner surface of an extended 2” (5 cm) or 2 ½” (6.4 cm) jacketing flap..

FASTENER OPTIONS:

STANDARD FASTENER “WIRETWISTS”: A stainless steel wire 20 Gauge (0.5 mm2) will be doubled up and twisted in a spiral fashion, with a minimum of 5-7 twists/Inch (2-3 twists/cm). Wiretwist Fastener length will be 16” (40 cm). The Wiretwist Fastener will be secured to the lacing pin at the pin stem. Pin stems will be 14 gauge (2.5 mm2). Wiretwist Fasteners will be spaced at most 6” (15 cm) on center along closing seams with matching lacing pins for securing.

Blanket Design Warranty:
Shannon Heat Shield Insulation will accommodate vibration probes, gauges, tubing, piping, brackets, etc. and fit correctly for optimum performance as per the design specification provided in the quotation process. In addition, for 18 months thermal blanket manufacturer will cover the cost of replacing the blanket should the failure be due to premature degradation of any component utilized in the blanket construction, as well as any defects due to poor workmanship.

SELECT YOUR: Testing Requirements

ASTM C 335	Standard Test Method for Steady-State Heat Transfer Properties of Pipe Insulation.

ASTM E 1222 – 90	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation - USA

ISO 15665	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation – Int’l

ASTM C 1045 – 07	Standard Practice for Calculating Thermal Transmission Properties under steady state conditions

UL 1709		Standard Fire Test of Protection Materials for MOV / Structural Steel

ASTM E-84-17	Surface Burning Characteristics of Building Materials (Flame Spread & Smoke)

ASTM E-136	Combustion Characteristics of Building Materials / Fire Test Response

ASTM D3787	Burst Strength Evaluation for ASTM F1138 – Spray Shield Compliance