Thermal Blanket Design: LT550LFP-FG (LT288C-LFP-FG)

Applications: Shannon Thermal Blanket Applications include; Sanitary Valves, Flanges, Pumps, Instrumentation, Equipment and Complex Surfaces that otherwise are left untreated. Addressing Radiant Heat Loss in a “Wash-Down” condition. Shannon-INSULTECH® Thermal Blanket Markets include; Food Processing, Chemical and Petro Chemical Processing Plants.

Service: Steam & Hot Water Applications, Food Grade, Wash-Down, Sanitary Conditions

Maximum Service Temperature: 288˚C (550˚F)

Purpose: Shannon Thermal Blankets are a CAD designed, CNC produced, high quality pre-engineered insulation system designed to save energy, retain radiant heat, minimize insulation maintenance and improve the surrounding work environment. Shannon Thermal Blankets are capable of withstanding severe weather and chemical environments. Shannon Thermal Blankets are flexible, easy to install, easy to remove and reinstall allowing quick access and easy equipment serviceability. The key benefit is “Re-Usability”.

Blanket Components: The Outer and Inner Non-Porous Jacketing is a 459 g/m² (13.5 oz/yd²) 100 percent PTFE Laminate. The Insulation Core Material is a 176.2 kg/m3 (11 lb/CF) Fiberglass Needled Mat - Type “E” Fiber. The Fiberglass Mat is encapsulated by the PTFE Jacketing and sewn together, producing a “Self-Contained Blanket System”, highly corrosive resistant. The Shannon Blanket System includes Integral Fasteners for install & removal.

Blanket Construction: Blanket construction shall be a “Double Sewn” lock stitch with a minimum 4.3 stitches per CM. All raw jacket edges will have a tri-fold PTFE Teflon® Laminate binding. No raw cut jacket edge will be exposed. Stitching will be pure Teflon® 3-Ply thread. “Heat Sealing Technology” will be applied on critical closure seams to minimize perforations and critical seam exposure. No “On-Site Fabrication” to assure high quality.

ID Plate: For easy identification and location, a stainless steel or aluminum name plate tag is riveted to each blanket piece.

Design Approach: Thermal Blankets will be custom fit to match each specific component geometry. “Generic Designs” are not acceptable. Thermal Blankets will be a self-contained insulation system with an integral fastener to allow for easy access, removal and re-installation.

Blanket Weight: Any one piece will not exceed 40lbs (18 KG) in weight.

Blanket Overlap: Thermal blanket will extend beyond the mating flange onto existing insulation for a minimum of 2” (5CM). Fitting sizes 6” or more must have a minimum 4” (10CM) overlap. Open gaps are not acceptable.

Leak Accommodations:  To accommodate a leak and detect its origin, blankets will have a low point stainless steel drain grommet or the design will incorporate a mating seam at the lowest point of the blanket.

CAD / CNC Requirement: Thermal Blanket Insulation will require CAD Drawing Submittals to assure accuracy of design. Upon receipt of project contract, each item must be field measured, tagged and “Custom Fitted” to assure a quality fit and finish. All blankets are to be CAD designed / CNC produced to assure the highest quality, precise fit and electronic CAD filing retrieval for future replacement.

Manufacture Origin:  Blanket & Blanket Components must be made in the U.S.A.

SELECT YOUR: FASTENER

STANDARD “WIRETWIST” FASTENER

A stainless steel wire 0.50 mm2 (20 Gauge) will be doubled up and twisted in a spiral fashion, with a minimum of 5-7 twists/inch (3-4 twists/CM). Wiretwist length will be 16” (40CM) or longer. The Wiretwist will be secured to the lacing pin at the pin stem. Pin stems will be 2.5 mm2 (14 gauge). Wiretwists will be spaced 6” (15CM) on center along closing seams with matching lacing pins to lace and secure to.

FASTENING OPTIONS:

2.) Stainless Steel Double “D” Ring Strap

A 1.5”(3.8CM) wide LFP composite 20 mil thick Strap 4-3/4” (12CM) overall long stationary strap is folded with two 1.5”(3.8CM) in width stainless steel “D” rings heat sealed to the outer surface of the jacket. This is placed ½” (1CM) from the closing seam edge. The pull down strap, minimally 14” (36CM) long, of the same material is heat sealed to the outer jacket 3” (4.8CM)  in from the closing seam edge. Both matching straps are spaced along the closing seam edge no greater than 8” (20CM) apart. All closing seams have a 1.5”(3.8CM) extended LFP flap, which is placed along the stationary strap side of the closing seam.

3.) Non-Metallic Side Release Buckle and Strap

The blanket fasteners will be 1 1/2” Delrin Side Release Buckles with 1.5”wide LFP composite 20 mil thick Straps. The Buckle strap will be a minimum of 5-1/2” long and will be heat sealed to the outer surface for a minimum of 5” in length. A matching pull strap will also be heat sealed on the outer jacket surface and will match up to the Buckle Strap. The pull strap will be a minimum of 14”.

Blanket Design Warranty:

Thermal Blankets will accommodate vibration probes, gauges, tubing, piping, brackets, etc. and fit correctly for optimum performance as per the design specification provided in the quotation process. In addition, for 18 months thermal blanket manufacturer will cover the cost of replacing the blanket should the failure be due to premature degradation of any component utilized in the blanket construction, as well as any defects due to poor workmanship.

SELECT YOUR: Testing Requirements

ASTM C 335	Standard Test Method for Steady-State Heat Transfer Properties of Pipe Insulation.

ASTM E 1222 – 90	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation - USA

ISO 15665	Standard Test Method for the Laboratory Measurement of the Insertion Loss of Pipe Insulation – Int’l

ASTM C 1045 – 07	Standard Practice for Calculating Thermal Transmission Properties under steady state conditions

UL 1709		Standard Fire Test of Protection Materials for MOV / Structural Steel

ASTM E-84-17	Surface Burning Characteristics of Building Materials (Flame Spread & Smoke)

ASTM E-136	Combustion Characteristics of Building Materials / Fire Test Response

ASTM D3787	Burst Strength Evaluation for ASTM F1138 – Spray Shield Compliance

# Text boxes

| Blanket Thickness Surface Temperature Reference: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Operating Temperature | Thickness | Surface Temperature | Thickness | Surface Temperature | Thickness | Surface Temperature |
| 121˚ C (250˚ F) | 25 mm( 1") | 37.9˚ C (100.2˚ F) | 40 mm( 1.5") | 33.3˚ C (92.0˚ F) | 50 mm (2") | 30.8˚ C (87.4˚ F) |
| 149˚ C (300˚ F) | 25 mm( 1") | 42.6˚ C (108.6˚ F) | 40 mm (1.5") | 36.8˚ C (98.2˚ F) | 50 mm (2") | 33.5˚ C (92.3˚ F) |
| 177˚ C (350˚ F) | 25 mm( 1") | 47.3 ˚C (117.2˚ F ) | 40 mm (1.5") | 40.3˚ C (104.6˚ F ) | 50 mm (2") | 36.3˚ C (97.4˚ F ) |
| 204˚ C (400˚ F) | 25 mm( 1") | 52.2˚ C (126.0˚ F) | 40 mm (1.5") | 44.0 ˚C (111.2˚ F) | 50 mm (2") | 39.3 ˚C (102.7˚ F) |
| 232˚ C (450˚ F) | 25 mm( 1") | 57.2 ˚ C (135.1˚ F) | 40 mm (1.5") | 47.8 ˚C (118.0˚ F) | 50 mm (2") | 42.3 ˚C (108.2˚ F) |
| 260˚ C (500˚ F) | 25 mm( 1") | 62.5˚ C (144.5˚ F) | 40 mm (1.5") | 51.7 ˚C (125.1˚ F) | 50 mm (2") | 45.5 ˚C (113.9˚ F) |
| 287.8˚ C (550˚ F) | 25 mm( 1") | 67.9˚ C (154.2˚ F) | 40 mm (1.5") | 55.8 ˚C (132.4˚ F) | 50 mm (2") | 48.9 ˚C (119.9˚ F) |
| * The above referenced Cold Face Surface Temperatures should be used as guidelines for blanket insulation thickness design. |
| * The Cold Face Surface Temperature of the blanket should approach surrounding ambient temperature conditions. |
| * The economic thickness of the blanket should consider blanket cost, thermal performance and blanket design constraints. |
| * Heat Loss Calculations are based on a 21.1˚ C (70˚ F) ambient temperature using a flat surface condition. |  |